## Uplink Decoder 2
Order | Device Type | Paste Downlink below
1 | ABM | Starts with "1x0E" | Protocol | Packet# | Message type | Event type
2 | ABM | 1a0e01 | 1 | 10 | ABM | Stopped
3 | ATH | Starts with "1x0D" | Protocol | Packet# | Message type | Event type | Temp dec C | Humidity %
4 | ATH | 1b0d080b304c90 | 1 | 11 | ATH | - Change in Humid | 11.3 | 76.9
5 | Contact | Starts with "1x07" | Protocol | Packet# | Message type | Contact State
6 | Contact | 150701 | 1 | 5 | CONTACT | Open
7 | Device Info Message | Starts with "1xFA" | Protocol | Packet# | Message type | Event type | Message
8 | Device Info Message | 15fa550800781400000000 | 1 | 5 | Device Info Message | Message 5 of 5 | 0800781400000000
9 | Door Window | Starts with "1x03" | Protocol | Packet# | Message type | Magnet state
10 | Door Window | 150301 | 1 | 5 | DOOR_WINDOW | Absent
11 | Downlink Ack | Starts with "1xFF" | Protocol | Packet# | Message type | ACK & Result | Reply
12 | Downlink Ack | 15ff03fc00011100000000 | 1 | 5 | DOWNLINK_ACK | Valid & next byte is reply | fc00011100000000
13 | IAQ Periodic | Starts with "1x34" | Protocol | Packet# | Message type | Temperature (C) | Humidity (%) | CO2 (PPM) | PM 1.0 (PPM) | PM 2.5 (PPM)
14 | IAQ Periodic | 1234000A05000a000b000c | 1 | 2 | Air Quality Periodic | 1 | 5 | 10 | 11 | 12
15 | IAQ Periodic Extended | Starts with "1x35" | Protocol | Packet# | Message type | PM 4.0 (PPM) | PM 10.0 (PPM) | VOC (PPM) | NoX (PPM)
16 | IAQ Periodic Extended | 15350001000200030004 | 1 | 5 | Air Quality Periodic Extended | 1 | 2 | 3 | 4
17 | IAQ Sensor | Starts with "1x33" | Protocol | Packet# | Message type | Event type | Sensor value
18 | IAQ Sensor | 10331050101 | 1 | 0 | Air Quality Sensor | PM2.5 > upper threshold | 20496
19 | Link Quality | Starts with "1xFB" | Protocol | Packet# | Message type | Current Subband | RSSI of last downlink | SNR of last downlink
20 | Link Quality | 17fb008af9 | 1 | 7 | LINK_QUALITY | 0 | -118 | -7
21 | Pulse Counter | Starts with "1x04" | Protocol | Packet# | Message type | Event type | Fractional Rate | Pulse rate integer | Pulse count [36:0]
22 | Pulse Counter | 140422333444444444 | 1 | 4 | Pulse Counter | Overspeed | 0.25 | 1587 | 18325193796
23 | Push Button | Starts with "1x06" | Protocol | Packet# | Message type | Button ID | Button action
24 | Push Button | 15060301 | 1 | 5 | PUSH_BUTTON | 03 | Released
25 | Reset | Starts with "1x00" | Protocol | Packet# | Message type | Device Type | Hardware version | Software version | Reset Code
26 | Reset | 1d000A308C460001 | 1 | 13 | RESET | Water Sensor | 3.0 | 3.2.6 | 00000000,00000001
27 | Sensor420mA | Starts with "1x11" | Protocol | Packet# | Message type | Event type | Current in 10mA units
28 | Sensor420mA | 1b110001bd | 1 | 11 | SENSOR420MA | Periodic | 4.45 mA
29 | Supervisory | Starts with "1x01" | Protocol | Packet# | Message type | Tamper since last reset | Tamper state | Downlink Error | Low batt | Ratio error | Current sensor state | Battery level | Current sensor state (Hex) | Event accumulation count
30 | Supervisory | 1e01111331000000000012 | 1 | 14 | SUPERVISORY | Yes | No | No | No | Yes | 00010011 | 3.1V | 00000000 | 18
31 | Tamper | Starts with "1x02" | Protocol | Packet# | Message type | Chassis state
32 | Tamper | 190200 | 1 | 9 | TAMPER | Open
33 | Temp External | Starts with "1x09" | Protocol | Packet# | Message type | Event type | Temp dec C
34 | Temp External | 1BDB93A9CB | 1 | 11 | #N/A | Change Decrease | -87
35 | Temp Internal | Starts with "1x19" | Protocol | Packet# | Message type | Event type | Temp dec C
36 | Temp Internal | 1c19008170 | 1 | 12 | CMOS TEMPERATURE EVNET | Periodic | -1.7
37 | Thermocouple | Starts with "1x13" | Protocol | Packet# | Message type | Event type | Temperature | Cold-junction temperature is outside of the normal operating range | Hot junction temperature is outside of the normal operating range | Cold-junction temperature is at or above than the cold-junction temperature high threshold | Cold-junction temperature is lower than the cold-junction temperature low threshold | Thermocouple temperature is too high | Thermocouple temperature is too low | Input voltage is negative or greater than VDD | Open circuit such as broken thermocouple wires has been detected
38 | Thermocouple | 101302F06087 | 1 | 0 | THERMOCOUPLE | Through Lower | -250 | Yes | No | No | No | No | Yes | Yes | Yes
39 | Tilt | Starts with "1x0A" | Protocol | Packet# | Message type | Event type | Angle in Degrees from Vertical
40 | Tilt | 170a0355 | 1 | 7 | TILT | Toward Horizontal | 85
41 | Ultrasonic | Starts with "1x10" | Protocol | Packet# | Message type | Event type | Distance in mm
42 | Ultrasonic | 1010000076 | 1 | 0 | ULTRASONIC | Periodic | 118
43 | Voltmeter | Starts with "1x14" | Protocol | Packet# | Message type | Event type | Current in 10mA units
44 | Voltmeter | 1214020006 | 1 | 2 | VOLTMETER | Through Lower | 0.6 mV
45 | Water | Starts with "1x08" | Protocol | Packet# | Message type | Water State | Water value
46 | Water | 19080100 | 1 | 9 | WATER | Not present | 0
Note on B1: Filter to your device message type here.

## Uplink Message Types (hidden)
Value | Type | Info1 | Bits1 | Info2 | Bits2 | Info3 | Bits3 | Info4 | Bits4 | Info5 | Bits5 | Info6 | Bits6 | Info7 | Bits7
00 | RESET | Device type code | 8 | Hardware version | 8 | Firmware version | 16 | Reset code | 16
01 | SUPERVISORY | Error codes (Bits 7-5 not used, 4 Tamper since last reset, 3 Tamper state, 2 Downlink error, 1 Low batt, 0 Radio error) | 8 | Current sensor state | 8 | Battery level | 8 | Current sensor state | 32 | Event Accumulation Count | 16
02 | TAMPER | Chassis state (0 open, 1 closed) | 8
03 | DOOR_WINDOW | Magnet state (0 present, 1 absent) | 8
06 | PUSH_BUTTON | Button ID (0x03 = 1) | 8 | Button Action (0x00 pressed, 0x01 released, 0x02 held) | 8
07 | CONTACT | Contact (0x00 shorted, 0x01 open) | 8
08 | WATER | Water (0x00 present, 0x01 not) | 8 | Water value 0-255 | 8
09 | TEMPERATURE | Event type (00 periodic, 01 through upper, 02 through lower, 03 change increase, 04 change decrease) | 8 | Temp deg C (2's compliment) | 8
0A | TILT | Event type (00 to vert, 01 to horiz, 02 toward vert, 03 toward horiz) | 8 | Angle in deg from vert (0-180) | 8
0D | ATH | Event type (00 periodic, 01 T > upper, 02 T < lower, 03 dT+, 04 dT-, 05 H > Upper, 06 H< lower, 07 dH+, 08 dH-) | 8 | Temp integer deg C, first bit is sign 0=+ | 8 | Temp decimal, 0.0-0.9 | 8 | Humidity integer % | 8 | Humidity decimal, 0.0-0.9 | 8
0E | ABM | Movement (00 Started, 01 Stopped) | 8
0F | TILT_HP (OBS) | Reporting type (00 Periodic, 01 To Vert, 02 to Horiz, 03 toward vert, 04 toward Horiz) | 8 | Integer of Angle 0-180 | 8 | Tenths of Angle, 0-9 | 8 | Temp in C, 0x10 means +16° C and 0x90 means -16° C | 16
10 | ULTRASONIC | Event type (00 periodic, 01 through upper, 02 through lower, 03 change increase, 04 change decrease) | 8 | Distance in mm 16b unsigned | 16
11 | SENSOR420MA | Event type (00 periodic, 01 through upper, 02 through lower, 03 change increase, 04 change decrease) | 8 | Current in 10mA units. This is a 16-bit positive integer ranging from 400-2000. For example, if the value is 0x0385, the current is 9.01mA. | 16
13 | THERMOCOUPLE | Event type (00 periodic, 01 through upper, 02 through lower, 03 change increase, 04 change decrease) | 8 | Current Temperature in degrees Celsius. Decoded by taking the 16-bit two’s complement number and multiplying by 1/16th. For example, if the value is 0x55C0 the temperature is 1372.00 degrees C. A value of 0xF060 would be -250.00 degrees. | 16 | Fault codes: Bit Position / Description 7 The cold-junction temperature is outside of the normal operating range. 6 The hot junction temperature is outside of the normal operating range. 5 The cold-junction temperature is at or above than the cold-junction temperature high threshold. 4 The cold-junction temperature is lower than the cold-junction temperature low threshold. 3 The thermocouple temperature is too high. 2 The thermocouple temperature is too low. 1 The input voltage is negative or greater than VDD. 0 An open circuit such as broken thermocouple wires has been detected | 8
14 | VOLTMETER | Event type (00 periodic, 01 through upper, 02 through lower, 03 change increase, 04 change decrease) | 8 | Voltage measurement in units of 10mV. This is a 16-bit positive integer ranging from 0-3000. For example, a value of 0x512 would be 12.98VDC. | 16
15 | CUSTOM_SENSOR
16 | GPS (OBS)
17 | HONEYWELL5800 (OBS)
18 | MAGNETOMETER (OBS)
19 | CMOS TEMPERATURE EVNET | Event type (00 periodic, 01 through upper, 02 through lower, 03 change increase, 04 change decrease) | 8 | Temp integer deg C, first bit is sign 0=+ | 8 | Temp decimal, 0.0-0.9 | 8
1A | VIBRATION_HB (OBS)
1C | VIBRATION_CH1 (OBS)
1D | VIBRATION_CH2 (OBS)
1E | VIBRATION_CH3 (OBS)
1F | VIBRATION_CH4 (OBS)
20 | VIBRATION_FFT (OBS)
33 | Air Quality Sensor | 0: Temp > upper threshold 1: Temp < lower threshold 2: Temp RoC increase 3: Temp RoC decrease 4: Humidity > upper threshold 5: Humidity < lower threshold 6: Humidity RoC increase 7: Humidity RoC decrease 8: CO2 > upper threshold 9: CO2 < lower threshold 10: CO2 RoC increase 11: CO2 RoC decrease 12: PM1.0 > upper threshold 13: PM1.0 < lower threshold 14: PM1.0 RoC increase 15: PM1.0 RoC decrease 16: PM2.5 > upper threshold 17: PM2.5 < lower threshold 18: PM2.5 RoC increase 19: PM2.5 RoC decrease 20: PM4.0 > upper threshold 21: PM4.0 < lower threshold 22: PM4.0 RoC increase 23: PM4.0 RoC decrease 24: PM10.0 > upper threshold 25: PM10.0 < lower threshold 26: PM10.0 RoC increase 27: PM10.0 RoC decrease 28: VOC > upper threshold 29: VOC < lower threshold 30: VOC RoC increase 31: VOC RoC decrease 32: NoX > upper threshold 33: Nox < lower threshold 34: NoX RoC increase 35: NoX RoC decrease | 8 | Sensor value | 16
34 | Air Quality Periodic | Temperature in C 2's comp, 1/10 | 16 | Humidity in % | 8 | CO2 in PPM | 16 | PM1.0 value in PPM | 16 | PM 2.5 value in PPM | 16
35 | Air Quality Periodic Extended | PM 4.0 value in PPM | 16 | PM 10.0 value in PPM | 16 | VOC in PPM | 16 | NoX in PPM | 16
FA | Device Info Message | Index of Device Configuration (0x15 reads as 1 of 5) | 8 | Configuration information (valid downlink) | 64
FB | LINK_QUALITY | Current Sub-Band | 8 | RSSI if last downlink, signed integer in 2's compliment format | 8 | SNR if last downlink, signed integer in 2's compliment format | 8
FC | RATE_LIMIT_EXCEEDED (OBS)
FD | TEST_MESSAGE (OBS)
FF | DOWNLINK_ACK | Ack & result (00 Not used, 01 Invalid, 02 Valid, 03 Valid & next byte has downlink RX) | 8 | Valid Downlink bytes as received. Follows 0x03 in first byte only | 64
04 | Pulse Counter | Event type / Fractional pulse rate | 8 | Pulse rate integer portion | 8 | Pulse count [39:32] | 8 | Pulse count [31:24] | 8 | Pulse count [23:16] | 8 | Pulse count [15:8] | 8 | Pulse count [7:0] | 8
case | DEVICE_TYPE in Reset
01 | Door/Window Sensor
02 | Door/Window High Security
03 | Contact Sensor
04 | No-Probe Temperature Sensor
05 | External-Probe Temperature Sensor
06 | Single Push Button
07 | Dual Push Button
08 | Acceleration-Based Movement Sensor
09 | Tilt Sensor
0A | Water Sensor
0B | Tank Level Float Sensor
0C | Glass Break Sensor
0D | Ambient Light Sensor
0E | Air Temperature and Humidity Sensor
0F | High-Precision Tilt Sensor
10 | Ultrasonic Level Sensor
11 | 4-20mA Current Loop Sensor
12 | Ext-Probe Air Temp and Humidity Sensor
13 | Thermocouple Temperature Sensor
14 | Voltage Sensor
15 | Custom Sensor
16 | GPS
17 | Honeywell 5800 Bridge
18 | Magnetometer
19 | Temperature - ath INTernal
1A | Compass
1B | Vaisala Weather Station
1C | Vibration sensor high bandwicth Chan1
1D | Vibration sensor high bandwicth Chan2
1E | Vibration sensor high bandwicth Chan3
1F | Vibration sensor high bandwicth Chan4
20 | Vibration sensor high bandwicth condensed fft
21 | Fridgebee shake-to-send
22 | Pulse counter
23 | DWS+ATH
24 | Indoor Air Quality

## Downlink Encoder
Order | Result | Device type | Filter, don't sort
1 | Generated DL | 4-20mA | Report on Change/Threshold | Periodic Reporting interval | Periodic Reporting value | Restoral Margin | Lower Threshold / increase (0.01 steps) | Upper Threshold / decrease (0.01 steps) | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Generated DL
2 | 1100FFFFFFFFFFFF | 4-20mA | Threshold | Minutes | 127 | 2.55 | 655.35 | 655.35 | 11 | 00 | FF | FF | FFFF | FFFF | 1100FFFFFFFFFFFF
3 | Generated DL | ABM | Acceleration Change Threshold | Settling time (250mS units) | Acceleration scaling factor | Enable movement stopped events | Enable movement started events | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
4 | 0E7FFF0000000000 | ABM | 127 | 63.75 | +/-2g | Yes | Yes | 0E | 7F | FF | 00 | 00 | 0E7FFF0000000000
5 | Generated DL | ADR Advanced | ADR ACK limit Unconfirmed mode | ADR ACK delay Unconfirmed mode | ADR ACK limit Confirmed mode | ADR ACK delay Confirmed mode | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
6 | EF40200201000000 | ADR Advanced | 255 | 255 | 255 | 255 | EF | FF | FF | FF | FF | EFFFFFFFFF000000
7 | Generated DL | Advanced | Rate limit | Port number | Link Quality reporting interval | Link Quality reporting value | DL_ID | Info1 | Info2 | Info3 | Generated DL
8 | 600516520080030000F2302C39C3A67A563B | Advanced | 0 | 0 | Minutes | 1 | FC | 00 | 00 | 81 | FC00008100000000
9 | Generated DL | Air Temp Humidity | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease | Temp restoral margin | Humidity restoral margin | Lower Humidity Threshold / Humidity increase | Upper Humidity Threshold / Humidity decrease | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Info6 | Info7 | Generated DL
10 | 0D017FFF80806464 | Air Temp Humidity | Report on Change | Yes | Hours | 127 | -128 | -128 | 15 | 15 | 100 | 100 | 0D | 01 | 7F | FF | 80 | 80 | 64 | 64 | 0D017FFF80806464
11 | Generated DL | Door Window | Enable Events | Open hold time Seconds (in 250mS steps) | Closed hold time Seconds (in 250mS steps) | DL_ID | Info1 | Info2 | Info3 | Generated DL
12 | 0300FFFFFFFF0000 | Door Window | Yes | 16383.75 | 16383.75 | 03 | 00 | FFFF | FFFF | 0300FFFFFFFF0000
13 | Generated DL | Dry Contact | Enable Contact closed events | Enable Contact open events | Shorted hold time (in 250mS stepps) | Open hold time (in 250mS stepps) | DL_ID | Info1 | Info2 | Info3 | Generated DL
14 | 0701FFFFFFFF0000 | Dry Contact | No | Yes | 16383.75 | 16383.75 | 07 | 01 | FFFF | FFFF | 0701FFFFFFFF0000
15 | Generated DL | General | Enable All Events | Enable Adaptive Data Rate | Use Confirmed Messages | Number of Retries | Supervisory reporting interval | Supervisory Period value | Sampling Time interval | Sampling Time value | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
16 | 600516520080030000F2302C39C3A67A563B | General | Yes | Yes | No | 1 | Minutes | 1 | mS | 150000 | 01 | 00 | 06 | 81 | #NUM! | #NUM!
17 | Generated DL | Link Quality | Number of failed confirmed message transmits before a rejoin. 1-255, 0 disables | DL_ID | Info1 | Generated DL
18 | ee06000000000000 | Link Quality | 1 | EE | 01 | EE01
19 | Generated DL | Push button | Enable hold | Enable released | Enable pressed | Hold delay (in 250mS stepps) | LED Blink on confirmed | LED blink on send | LED when pressed | DL_ID | Info1 | Info2 | Info3 | Generated DL
20 | 0606FF0400000000 | Push button | No | No | Yes | 63.75 | No | Yes | Yes | 06 | 06 | FF | 04 | 0606FF0400000000
21 | Generated DL | Rejoin | Enable discard packets | Enable inportant messages | Enable retain subband | Subband Retries | Message discards | DL_ID | Info1 | Info2 | Info3 | Generated DL
22 | ea01ff0500000000 | Rejoin | No | Yes | Yes | 255 | 255 | EA | 04 | FF | FF | EA04FFFF00000000
23 | Generated DL | Temp External | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Temp restoral margin | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Generated DL
24 | 09017F0F807F0000 | Temp External | Report on Change | Yes | Hours | 127 | 15 | -128 | 127 | 09 | 01 | 7F | 0F | 80 | 7F | 09017F0F807F0000
25 | Generated DL | Temp Internal | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Temp restoral margin | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Generated DL
26 | 1900FF0F807F0000 | Temp Internal | Threshold | Yes | Minutes | 127 | 15 | -128 | 127 | 19 | 00 | FF | 0F | 80 | 7F | 1900FF0F807F0000
27 | Generated DL | Thermocouple | Thermocouple type | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Restoral Margin | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Generated DL
28 | 1331FFFFF80007F0 | Thermocouple | K | Report on Change | Yes | Minutes | 127 | 255 | -128 | 127 | 13 | 31 | FF | FF | F800 | 07F0 | 1331FFFFF80007F0
29 | Generated DL | Tilt | Enable report on change (ROC) to Vertical | Enable ROC to Horizontal | Enable transitions to Vertical | Enable transitions to Horizontal | Angle for transition to Horizontal | Angle for transition to vertical | Vertical hold time (250mS units) | Horizontal hold time (250mS units) | ROC towards Vertical (5-90, 0-4 disables) | ROC towards Horizontal (5-90, 0-4 disables) | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Info6 | Info7 | Generated DL
30 | 0A085A5AFFFF5A5A | Tilt | No | Yes | Yes | Yes | 90 | 90 | 63.75 | 63.75 | 90 | 90 | 0A | 08 | 5A | 5A | FF | FF | 5A | 5A | 0A085A5AFFFF5A5A
31 | Generated DL | Voltmeter | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Restoral margin 10mV - 2.55V 0 disables | Lower Voltage Threshold / V increase | Upper Voltage Threshold / V decrease | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Generated DL
32 | 1400FFFFFFFFFFFF | Voltmeter | Threshold | Yes | Minutes | 127 | 2.55 | 655.35 | 655.35 | 14 | 00 | FF | FF | FFFF | FFFF | 1400FFFFFFFFFFFF
33 | Generated DL | Water | Enable Events | Threshold | Restoral Margin | DL_ID | Info1 | Info2 | Info3 | Generated DL
34 | 0800FFFF00000000 | Water | Yes | 255 | 255 | 08 | 00 | FF | FF | 0800FFFF00000000
35 | Generated DL | Advanced IAQ | Pressure Sampling Period | CO2 Sampling Period | ATH Sampling Period | ATH Reporting interval | ATH Periodic Reporting value | CO2 Reporting interval | CO2 Periodic Reporting value | Pressure Reporting interval | Pressure Periodic Reporting value | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
36 | 3107FF7F7F000000 | Advanced IAQ | Update | Update | Update | Minutes | 127 | Hours | 127 | Hours | 127 | 31 | 07 | FF | 7F | 7F | 3107FF7F7F000000
37 | Generated DL | Advanced IAQ Radio | Port number | Link quality period | Link Quality reporting interval | Link quality attempts | Unconfirmed ADR ACK limit | Unconfirmed ADR ACK delay | Confirmed ADR ACK limit | Confirmed ADR ACK delay | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Info6 | Info7 | Info8
38 | 327FFFFFFFFFFFFF00 | Advanced IAQ Radio | 127 | Minutes | 127 | 255 | 255 | 255 | 255 | 255 | 32 | 7F | FF | FF | FF | FF | FF | FF | 327FFFFFFFFFFFFF00
39 | Generated DL | Air Temp & Humidity Sensor Report on Change Configuration | Enable report on change (ROC) reporting | Temperature Decrease | Temperature Increase | Humidity Decrease | Humidity Increase | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Generated DL
40 | 3400FFFFFFFF0000 | Air Temp & Humidity Sensor Report on Change Configuration | No | 255 | 255 | 255 | 255 | 34 | 00 | FF | FF | FF | FF | 3400FFFFFFFF0000
41 | Generated DL | Air Temp & Humidity Sensor Threshold Configuration | Enable Threshold reporting | Temperature restoral margin | Lower Temperature threshold | Upper Temperature threshold | Humidity restoral margin | Lower Humidity threshold | Upper Humidity threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Info4 | Info5 | Generated DL
42 | 3300FFFFFFFFFFFF | Air Temp & Humidity Sensor Threshold Configuration | No | 255 | 255 | 255 | 255 | 255 | 255 | 33 | 00 | FF | FF | FF | FF | FF | FF | 3300FFFFFFFFFFFF
43 | Generated DL | CO2 Sensor Report on Change Configuration | Enable ROC reporting | CO2 Decrease | CO2 Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
44 | 3600FFFFFFFF0000 | CO2 Sensor Report on Change Configuration | No | 65535 | 65535 | 36 | 00 | FFFF | FFFF | 3600FFFFFFFF0000
45 | Generated DL | CO2 Sensor Threshold Configuration | Enable Threshold reporting | Expected CO2 value | Lower CO2 threshold | Upper CO2 threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
46 | 3501FFFFFFFFFFFF | CO2 Sensor Threshold Configuration | Yes | 65535 | 65535 | 65535 | 35 | 01 | FFFF | FFFF | FFFF | 3501FFFFFFFFFFFF
47 | Generated DL | Discard Packets | Discard backlog | DL_ID | Info1 | Generated DL
48 | EB01 | Discard Packets | Yes | EB | 01 | EB01
49 | Generated DL | General IAQ Configuration | Enable Events | Uplink retries | Confirmed uplinks | ADR | Super Reporting interval | Super Periodic Reporting value | Periodic Reporting interval | Periodic Periodic Reporting value | DL_ID | Info1 | Info2 | Info3 | Info4 | Info8
50 | 300020FFFF000000 | General IAQ Configuration | No | 8 | Yes | Yes | Minutes | 127 | Minutes | 127 | 30 | 00 | 20 | FF | FF | 300020FFFF000000
51 | Generated DL | NoX Sensor Report on Change Configuration | Enable ROC reporting | NoX Decrease | NoX Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
52 | 4200FFFFFFFF0000 | NoX Sensor Report on Change Configuration | No | 65535 | 65535 | 42 | 00 | FFFF | FFFF | 4200FFFFFFFF0000
53 | Generated DL | NoX Sensor Threshold Configuration | Enable Threshold reporting | Expected NoX value | Lower NoX threshold | Upper NoX threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
54 | 4101FFFFFFFFFFFF | NoX Sensor Threshold Configuration | Yes | 65535 | 65535 | 65535 | 41 | 01 | FFFF | FFFF | FFFF | 4101FFFFFFFFFFFF
55 | Generated DL | PM 1.0 Sensor Threshold Configuration | Enable Threshold reporting | Expected PM 1.0 value | Lower PM 1.0 threshold | Upper PM 1.0 threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
56 | 3700FFFFFFFFFFFF | PM 1.0 Sensor Threshold Configuration | No | 65535 | 65535 | 65535 | 37 | 00 | FFFF | FFFF | FFFF | 3700FFFFFFFFFFFF
57 | Generated DL | PM 1.0 Sensor Report on Change Configuration | Enable ROC reporting | PM 1.0 Decrease | PM 1.0 Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
58 | 3801FFFFFFFF0000 | PM 1.0 Sensor Report on Change Configuration | Yes | 65535 | 65535 | 38 | 01 | FFFF | FFFF | 3801FFFFFFFF0000
59 | Generated DL | PM 2.5 Sensor Threshold Configuration | Enable Threshold reporting | Expected PM 2.5 value | Lower PM 2.5 threshold | Upper PM 2.5 threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
60 | 3901FFFFFFFFFFFF | PM 2.5 Sensor Threshold Configuration | Yes | 65535 | 65535 | 65535 | 39 | 01 | FFFF | FFFF | FFFF | 3901FFFFFFFFFFFF
61 | Generated DL | PM 2.5 Sensor Report on Change Configuration | Enable ROC reporting | PM 2.5 Decrease | PM 2.5 Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
62 | 3A01FFFFFFFF0000 | PM 2.5 Sensor Report on Change Configuration | Yes | 65535 | 65535 | 3A | 01 | FFFF | FFFF | 3A01FFFFFFFF0000
63 | Generated DL | PM 4.0 Sensor Threshold Configuration | Enable Threshold reporting | Expected PM 4.0 value | Lower PM 4.0 threshold | Upper PM 4.0 threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
64 | 3B01FFFFFFFFFFFF | PM 4.0 Sensor Threshold Configuration | Yes | 65535 | 65535 | 65535 | 3B | 01 | FFFF | FFFF | FFFF | 3B01FFFFFFFFFFFF
65 | Generated DL | PM 4.0 Sensor Report on Change Configuration | Enable ROC reporting | PM 4.0 Decrease | PM 4.0 Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
66 | 3C01FFFFFFFF0000 | PM 4.0 Sensor Report on Change Configuration | Yes | 65535 | 65535 | 3C | 01 | FFFF | FFFF | 3C01FFFFFFFF0000
67 | Generated DL | PM 10.0 Sensor Threshold Configuration | Enable Threshold reporting | Expected PM 10.0 value | Lower PM 10.0 threshold | Upper PM 10.0 threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
68 | 3D01FFFFFFFFFFFF | PM 10.0 Sensor Threshold Configuration | Yes | 65535 | 65535 | 65535 | 3D | 01 | FFFF | FFFF | FFFF | 3D01FFFFFFFFFFFF
69 | Generated DL | PM 10.0 Sensor Report on Change Configuration | Enable ROC reporting | PM 10.0 Decrease | PM 10.0 Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
70 | 3E01FFFFFFFF0000 | PM 10.0 Sensor Report on Change Configuration | Yes | 65535 | 65535 | 3E | 01 | FFFF | FFFF | 3E01FFFFFFFF0000
71 | Generated DL | Shake-to-send Configuration (Firmware 3.0 or newer) | Enable shake to send | Acceleration scaling factor | Motion threshold | Settling time (250mS units) | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
72 | 2001007FFF0000 | Shake-to-send Configuration (Firmware 3.0 or newer) | Yes | +/-2g | 127 | 63.75 | 20 | 01 | 00 | 7F | FF | 2001007FFF0000
73 | Generated DL | VOC Sensor Threshold Configuration | Enable Threshold reporting | Expected PM 10.0 value | Lower PM 10.0 threshold | Upper PM 10.0 threshold | DL_ID | Info1 | Info2 | Info3 | Info4 | Generated DL
74 | 3F01FFFFFFFFFFFF | VOC Sensor Threshold Configuration | Yes | 65535 | 65535 | 65535 | 3F | 01 | FFFF | FFFF | FFFF | 3F01FFFFFFFFFFFF
75 | Generated DL | VOC Sensor Report on Change Configuration | Enable ROC reporting | PM 10.0 Decrease | PM 10.0 Increase | DL_ID | Info1 | Info2 | Info3 | Generated DL
76 | 4001FFFFFFFF0000 | VOC Sensor Report on Change Configuration | Yes | 65535 | 65535 | 40 | 01 | FFFF | FFFF | 4001FFFFFFFF0000
77 | Generated DL | Pulse Counter | Periodic Reporting interval | Periodic Reporting value | Threshold sample size (groups of 5) | Restoral margin | Overspeed threshold | Underspeed threshold | Too-Long interval | Too-Long value | Debounce delay (increments of 5mS, 0 = leave unchanged) | DL_ID | Info1 | Info2 | Info3 | Info4 | Info5 | Info6 | Info7 | Info8 | Generated DL
78 | 04FFFF0FFF0FFFFF | Pulse Counter | Minutes | 127 | 75 | 15 | 4095 | 4095 | Minutes | 127 | 1275 | 04 | FF | FF | 0F | FF | 0F | FF | FF | FF | 04FFFF0FFF0FFFFF
Note on C1: Filter to your device message type here. Do not sort table!
Note on F3: Value between 1 & 127
Note on G3: Value between 0 & 2.55
Note on H3: Nick Klein: Milivolt resolution 0.01 thru 655.35
Note on I3: Nick Klein: Milivolt resolution 0.01 thru 655.35
Note on D5: Value between 1 & 127
Note on E5: Value between 0 & 63.75
Note on D7: Value between 0 & 255
Note on E7: Value between 0 & 255
Note on F7: Value between 0 & 255
Note on G7: Value between 0 & 255
Note on D9: Value between 0 & 255
Note on E9: Value between 0 & 255
Note on G9: Value between 1 & 127
Note on G11: Value between 1 & 127
Note on H11: Nick Klein: -128 to 127
Note on I11: Nick Klein: -128 to 127
Note on J11: Value between 0 & 15
Note on K11: Value between 0 & 15
Note on L11: Nick Klein: 0 to 100
Note on M11: Nick Klein: 0 to 100
Note on E13: Value between 0 & 16,383.75
Note on F13: Value between 0 & 16,383.75
Note on F15: Value between 0 & 16,383.75
Note on G15: Value between 0 & 16,383.75
Note on G17: Value from 0-7
Note on I17: Value between 1 & 127
Note on K17: mS from 250-150000 Sec/Min/Hours from 1-63
Note on D19: Value between 0 & 255
Note on G21: Value between 0 & 63.75
Note on G23: Value between 0 & 255
Note on H23: Value between 0 & 255
Note on G25: Value between 1 & 127
Note on H25: Value between 0 & 15
Note on I25: Nick Klein: -128 to 127
Note on J25: Nick Klein: -128 to 127
Note on G27: Value between 1 & 127
Note on H27: Value between 0 & 15
Note on I27: Nick Klein: -128 to 127
Note on J27: Nick Klein: -128 to 127
Note on H29: Value between 1 & 127
Note on I29: Value between 0 & 255
Note on J29: Nick Klein: -128 to 127
Note on K29: Nick Klein: -128 to 127
Note on H31: Value between 0-90
Note on I31: Value between 0-90
Note on J31: Value between 0 & 63.75
Note on K31: Value between 0 & 63.75
Note on L31: Value between 0-90
Note on M31: Value between 0-90
Note on G33: Value between 1 & 127
Note on H33: Value between 0 & 2.55
Note on I33: Nick Klein: Milivolt resolution 0.01 thru 655.35
Note on J33: Nick Klein: Milivolt resolution 0.01 thru 655.35
Note on E35: Value between 0 & 255
Note on F35: Value between 0 & 255
Note on H37: Value between 0 & 127
Note on J37: Value between 0 & 127
Note on L37: Value between 0 & 127
Note on D39: Value between 1 & 127
Note on F39: Value between 0 & 127
Note on G39: Value between 0 & 255
Note on H39: Value between 0 & 255
Note on I39: Value between 0 & 255
Note on J39: Value between 0 & 255
Note on K39: Value between 0 & 255
Note on E41: Value between 0 & 255
Note on F41: Value between 0 & 255
Note on G41: Value between 0 & 255
Note on H41: Value between 0 & 255
Note on E43: Value between 0 & 255
Note on F43: Value between 0 & 255
Note on G43: Value between 0 & 255
Note on H43: Value between 0 & 255
Note on I43: Value between 0 & 255
Note on J43: Value between 0 & 255
Note on E45: Value between 0 & 65535
Note on F45: Value between 0 & 65535
Note on E47: Value between 0 & 65535
Note on F47: Value between 0 & 65535
Note on G47: Value between 0 & 65535
Note on E51: Value between 1-8
Note on I51: Value between 0 & 127
Note on K51: Value between 0 & 127
Note on E53: Value between 0 & 65535
Note on F53: Value between 0 & 65535
Note on E55: Value between 0 & 65535
Note on F55: Value between 0 & 65535
Note on G55: Value between 0 & 65535
Note on E57: Value between 0 & 65535
Note on F57: Value between 0 & 65535
Note on G57: Value between 0 & 65535
Note on E59: Value between 0 & 65535
Note on F59: Value between 0 & 65535
Note on E61: Value between 0 & 65535
Note on F61: Value between 0 & 65535
Note on G61: Value between 0 & 65535
Note on E63: Value between 0 & 65535
Note on F63: Value between 0 & 65535
Note on E65: Value between 0 & 65535
Note on F65: Value between 0 & 65535
Note on G65: Value between 0 & 65535
Note on E67: Value between 0 & 65535
Note on F67: Value between 0 & 65535
Note on E69: Value between 0 & 65535
Note on F69: Value between 0 & 65535
Note on G69: Value between 0 & 65535
Note on E71: Value between 0 & 65535
Note on F71: Value between 0 & 65535
Note on F73: Value between 1 & 127
Note on G73: Value between 0 & 63.75
Note on E75: Value between 0 & 65535
Note on F75: Value between 0 & 65535
Note on G75: Value between 0 & 65535
Note on E77: Value between 0 & 65535
Note on F77: Value between 0 & 65535
Note on E79: Value between 0 & 127
Note on F79: Value between 0 & 75
Note on G79: Value between 0 & 15
Note on H79: Value between 0 & 4095
Note on I79: Value between 0 & 4095
Note on K79: Value between 0 & 127
Note on L79: Value between 0 & 2550

## Tables (hidden)
Milliseconds | ROC_Temp | ContactTime | ContactTimeHex | AMBSettlingTime | AMBSettlingTimeHex | AngleForTransition | HoldTime | AngleForReport | Thermocouple Type | Thermocouple code | IAQ message ID | IAQ message type | 0-2550 | 0-1275 | 0-75
250 | 1 | 0 Seconds | 0000 | 0.25 | 01 | 0 | 0 | 0 | B | 0000 | 00 | Temp > upper threshold | 0 | 0 | 0
500 | 2 | .25 Seconds | 0001 | 0.5 | 02 | 5 | 0.25 | 10 | E | 0001 | 01 | Temp < lower threshold | 10 | 5 | 5
750 | 3 | .5 Seconds | 0002 | 0.75 | 03 | 10 | 0.5 | 20 | J | 0010 | 02 | Temp RoC increase | 20 | 10 | 10
1000 | 4 | 1 Second | 0004 | 1 | 04 | 15 | 1 | 30 | K | 0011 | 03 | Temp RoC decrease | 30 | 15 | 15
1250 | 5 | 2 Seconds | 0008 | 2 | 08 | 20 | 2 | 40 | N | 0100 | 04 | Humidity > upper threshold | 40 | 20 | 20
1500 | 6 | 3 Seconds | 000C | 3 | C | 25 | 3 | 50 | R | 0101 | 05 | Humidity < lower threshold | 50 | 25 | 25
1750 | 7 | 4 Seconds | 0010 | 4 | 10 | 30 | 4 | 60 | S | 0110 | 06 | Humidity RoC increase | 60 | 30 | 30
2000 | 8 | 5 Seconds | 0014 | 5 | 14 | 35 | 5 | 70 | T | 0111 | 07 | Humidity RoC decrease | 70 | 35 | 35
2250 | 9 | 10 Seconds | 0028 | 6 | 18 | 40 | 10 | 80 | V Mode Gain 8 | 1000 | 08 | CO2 > upper threshold | 80 | 40 | 40
2500 | 10 | 30 Seconds | 0078 | 7 | 1C | 45 | 30 |  | V Mode Gain 32 | 1100 | 09 | CO2 < lower threshold | 90 | 45 | 45
2750 | 11 | 1 Minute | 00F0 | 8 | 20 | 50 | 60 |  |  |  | 0A | CO2 RoC increase | 100 | 50 | 50
3000 | 12 | 5 Minutes | 04FB | 9 | 24 | 55 |  |  |  |  | 0B | CO2 RoC decrease | 110 | 55 | 55
3250 | 13 | 10 Minutes | 0960 | 10 | 28 | 60 |  |  |  |  | 0C | PM1.0 > upper threshold | 120 | 60 | 60
3500 | 14 | 30 Minutes | 1C20 | 11 | 2C | 65 |  |  |  |  | 0D | PM1.0 < lower threshold | 130 | 65 | 65
3750 | 15 | 1 Hour | 3840 | 12 | 30 | 70 |  |  |  |  | 0E | PM1.0 RoC increase | 140 | 70 | 70
4000 |  | 2 Hours | 7080 | 13 | 34 | 75 |  |  |  |  | 0F | PM1.0 RoC decrease | 150 | 75 | 75
4250 |  | 3 Hours | A8C0 | 14 | 38 | 80 |  |  |  |  | 10 | PM2.5 > upper threshold | 160 | 80
4500 |  | 4 hours | 0002 | 15 | 3C | 85 |  |  |  |  | 11 | PM2.5 < lower threshold | 170 | 85
4750 |  |  |  | 16 | 40 | [5 empty] | 12 | PM2.5 RoC increase | 180 | 90
5000 |  |  |  | 17 | 44 | [5 empty] | 13 | PM2.5 RoC decrease | 190 | 95
5250 |  |  |  | 18 | 48 | [5 empty] | 14 | PM4.0 > upper threshold | 200 | 100
5500 |  |  |  | 19 | 4C | [5 empty] | 15 | PM4.0 < lower threshold | 210 | 105
5750 |  |  |  | 20 | 50 | [5 empty] | 16 | PM4.0 RoC increase | 220 | 110
6000 |  |  |  | 21 | 54 | [5 empty] | 17 | PM4.0 RoC decrease | 230 | 115
6250 |  |  |  | 22 | 58 | [5 empty] | 18 | PM10.0 > upper threshold | 240 | 120
6500 |  |  |  | 23 | 5C | [5 empty] | 19 | PM10.0 < lower threshold | 250 | 125
6750 |  |  |  | 24 | 60 | [5 empty] | 1A | PM10.0 RoC increase | 260 | 130
7000 |  |  |  | 25 | 64 | [5 empty] | 1B | PM10.0 RoC decrease | 270 | 135
7250 |  |  |  | 26 | 68 | [5 empty] | 1C | VOC > upper threshold | 280 | 140
7500 |  |  |  | 27 | 6C | [5 empty] | 1D | VOC < lower threshold | 290 | 145
7750 |  |  |  | 28 | 70 | [5 empty] | 1E | VOC RoC increase | 300 | 150
8000 |  |  |  | 29 | 74 | [5 empty] | 1F | VOC RoC decrease | 310 | 155
8250 |  |  |  | 30 | 78 | [5 empty] | 20 | NoX > upper threshold | 320 | 160
8500 |  |  |  | 31 | 7C | [5 empty] | 21 | Nox < lower threshold | 330 | 165
8750 |  |  |  | 32 | 80 | [5 empty] | 22 | NoX RoC increase | 340 | 170
9000 |  |  |  | 33 | 84 | [5 empty] | 23 | NoX RoC decrease | 350 | 175
9250 |  |  |  | 34 | 88 | [7 empty] | 360 | 180
9500 |  |  |  | 35 | 8C | [7 empty] | 370 | 185
9750 |  |  |  | 36 | 90 | [7 empty] | 380 | 190
10000 |  |  |  | 37 | 94 | [7 empty] | 390 | 195
10250 |  |  |  | 38 | 98 | [7 empty] | 400 | 200
10500 |  |  |  | 39 | 9C | [7 empty] | 410 | 205
10750 |  |  |  | 40 | A0 | [7 empty] | 420 | 210
11000 |  |  |  | 41 | A4 | [7 empty] | 430 | 215
11250 |  |  |  | 42 | A8 | [7 empty] | 440 | 220
11500 |  |  |  | 43 | AC | [7 empty] | 450 | 225
11750 |  |  |  | 44 | B0 | [7 empty] | 460 | 230
12000 |  |  |  | 45 | B4 | [7 empty] | 470 | 235
12250 |  |  |  | 46 | B8 | [7 empty] | 480 | 240
12500 |  |  |  | 47 | BC | [7 empty] | 490 | 245
12750 |  |  |  | 48 | C0 | [7 empty] | 500 | 250
13000 |  |  |  | 49 | C4 | [7 empty] | 510 | 255
13250 |  |  |  | 50 | C8 | [7 empty] | 520 | 260
13500 |  |  |  | 51 | CC | [7 empty] | 530 | 265
13750 |  |  |  | 52 | D0 | [7 empty] | 540 | 270
14000 |  |  |  | 53 | D4 | [7 empty] | 550 | 275
14250 |  |  |  | 54 | D8 | [7 empty] | 560 | 280
14500 |  |  |  | 55 | DC | [7 empty] | 570 | 285
14750 |  |  |  | 56 | E0 | [7 empty] | 580 | 290
15000 |  |  |  | 57 | E4 | [7 empty] | 590 | 295
|  |  |  | 58 | E8 | [7 empty] | 600 | 300
|  |  |  | 59 | EC | [7 empty] | 610 | 305
|  |  |  | 60 | F0 | [7 empty] | 620 | 310
|  |  |  | 61 | F4 | [7 empty] | 630 | 315
|  |  |  | 62 | F8 | [7 empty] | 640 | 320
|  |  |  | 63 | FC | [7 empty] | 650 | 325
[13 empty] | 660 | 330
[13 empty] | 670 | 335
[13 empty] | 680 | 340
[13 empty] | 690 | 345
[13 empty] | 700 | 350
[13 empty] | 710 | 355
[13 empty] | 720 | 360
[13 empty] | 730 | 365
[13 empty] | 740 | 370
[13 empty] | 750 | 375
[13 empty] | 760 | 380
[13 empty] | 770 | 385
[13 empty] | 780 | 390
[13 empty] | 790 | 395
[13 empty] | 800 | 400
[13 empty] | 810 | 405
[13 empty] | 820 | 410
[13 empty] | 830 | 415
[13 empty] | 840 | 420
[13 empty] | 850 | 425
[13 empty] | 860 | 430
[13 empty] | 870 | 435
[13 empty] | 880 | 440
[13 empty] | 890 | 445
[13 empty] | 900 | 450
[13 empty] | 910 | 455
[13 empty] | 920 | 460
[13 empty] | 930 | 465
[13 empty] | 940 | 470
[13 empty] | 950 | 475
[13 empty] | 960 | 480
[13 empty] | 970 | 485
[13 empty] | 980 | 490
[13 empty] | 990 | 495
[13 empty] | 1000 | 500
[13 empty] | 1010 | 505
[13 empty] | 1020 | 510
[13 empty] | 1030 | 515
[13 empty] | 1040 | 520
[13 empty] | 1050 | 525
[13 empty] | 1060 | 530
[13 empty] | 1070 | 535
[13 empty] | 1080 | 540
[13 empty] | 1090 | 545
[13 empty] | 1100 | 550
[13 empty] | 1110 | 555
[13 empty] | 1120 | 560
[13 empty] | 1130 | 565
[13 empty] | 1140 | 570
[13 empty] | 1150 | 575
[13 empty] | 1160 | 580
[13 empty] | 1170 | 585
[13 empty] | 1180 | 590
[13 empty] | 1190 | 595
[13 empty] | 1200 | 600
[13 empty] | 1210 | 605
[13 empty] | 1220 | 610
[13 empty] | 1230 | 615
[13 empty] | 1240 | 620
[13 empty] | 1250 | 625
[13 empty] | 1260 | 630
[13 empty] | 1270 | 635
[13 empty] | 1280 | 640
[13 empty] | 1290 | 645
[13 empty] | 1300 | 650
[13 empty] | 1310 | 655
[13 empty] | 1320 | 660
[13 empty] | 1330 | 665
[13 empty] | 1340 | 670
[13 empty] | 1350 | 675
[13 empty] | 1360 | 680
[13 empty] | 1370 | 685
[13 empty] | 1380 | 690
[13 empty] | 1390 | 695
[13 empty] | 1400 | 700
[13 empty] | 1410 | 705
[13 empty] | 1420 | 710
[13 empty] | 1430 | 715
[13 empty] | 1440 | 720
[13 empty] | 1450 | 725
[13 empty] | 1460 | 730
[13 empty] | 1470 | 735
[13 empty] | 1480 | 740
[13 empty] | 1490 | 745
[13 empty] | 1500 | 750
[13 empty] | 1510 | 755
[13 empty] | 1520 | 760
[13 empty] | 1530 | 765
[13 empty] | 1540 | 770
[13 empty] | 1550 | 775
[13 empty] | 1560 | 780
[13 empty] | 1570 | 785
[13 empty] | 1580 | 790
[13 empty] | 1590 | 795
[13 empty] | 1600 | 800
[13 empty] | 1610 | 805
[13 empty] | 1620 | 810
[13 empty] | 1630 | 815
[13 empty] | 1640 | 820
[13 empty] | 1650 | 825
[13 empty] | 1660 | 830
[13 empty] | 1670 | 835
[13 empty] | 1680 | 840
[13 empty] | 1690 | 845
[13 empty] | 1700 | 850
[13 empty] | 1710 | 855
[13 empty] | 1720 | 860
[13 empty] | 1730 | 865
[13 empty] | 1740 | 870
[13 empty] | 1750 | 875
[13 empty] | 1760 | 880
[13 empty] | 1770 | 885
[13 empty] | 1780 | 890
[13 empty] | 1790 | 895
[13 empty] | 1800 | 900
[13 empty] | 1810 | 905
[13 empty] | 1820 | 910
[13 empty] | 1830 | 915
[13 empty] | 1840 | 920
[13 empty] | 1850 | 925
[13 empty] | 1860 | 930
[13 empty] | 1870 | 935
[13 empty] | 1880 | 940
[13 empty] | 1890 | 945
[13 empty] | 1900 | 950
[13 empty] | 1910 | 955
[13 empty] | 1920 | 960
[13 empty] | 1930 | 965
[13 empty] | 1940 | 970
[13 empty] | 1950 | 975
[13 empty] | 1960 | 980
[13 empty] | 1970 | 985
[13 empty] | 1980 | 990
[13 empty] | 1990 | 995
[13 empty] | 2000 | 1000
[13 empty] | 2010 | 1005
[13 empty] | 2020 | 1010
[13 empty] | 2030 | 1015
[13 empty] | 2040 | 1020
[13 empty] | 2050 | 1025
[13 empty] | 2060 | 1030
[13 empty] | 2070 | 1035
[13 empty] | 2080 | 1040
[13 empty] | 2090 | 1045
[13 empty] | 2100 | 1050
[13 empty] | 2110 | 1055
[13 empty] | 2120 | 1060
[13 empty] | 2130 | 1065
[13 empty] | 2140 | 1070
[13 empty] | 2150 | 1075
[13 empty] | 2160 | 1080
[13 empty] | 2170 | 1085
[13 empty] | 2180 | 1090
[13 empty] | 2190 | 1095
[13 empty] | 2200 | 1100
[13 empty] | 2210 | 1105
[13 empty] | 2220 | 1110
[13 empty] | 2230 | 1115
[13 empty] | 2240 | 1120
[13 empty] | 2250 | 1125
[13 empty] | 2260 | 1130
[13 empty] | 2270 | 1135
[13 empty] | 2280 | 1140
[13 empty] | 2290 | 1145
[13 empty] | 2300 | 1150
[13 empty] | 2310 | 1155
[13 empty] | 2320 | 1160
[13 empty] | 2330 | 1165
[13 empty] | 2340 | 1170
[13 empty] | 2350 | 1175
[13 empty] | 2360 | 1180
[13 empty] | 2370 | 1185
[13 empty] | 2380 | 1190
[13 empty] | 2390 | 1195
[13 empty] | 2400 | 1200
[13 empty] | 2410 | 1205
[13 empty] | 2420 | 1210
[13 empty] | 2430 | 1215
[13 empty] | 2440 | 1220
[13 empty] | 2450 | 1225
[13 empty] | 2460 | 1230
[13 empty] | 2470 | 1235
[13 empty] | 2480 | 1240
[13 empty] | 2490 | 1245
[13 empty] | 2500 | 1250
[13 empty] | 2510 | 1255
[13 empty] | 2520 | 1260
[13 empty] | 2530 | 1265
[13 empty] | 2540 | 1270
[13 empty] | 2550 | 1275

## Downlink Decoder 2
Order | Device type | Paste Downlink below
110 | 4-20mA | Starts with "11" | Report on Change/Threshold | Periodic Reporting interval | Periodic Reporting value | Restoral Margin | Lower Threshold / increase | Upper Threshold / decrease
111 | 4-20mA | 11008A0A0017620C | Threshold | Minutes | 10 | 0.1 | 0.23 | 251
0E0 | ABM | Starts with "0E" | Acceleration Change Threshold | Settling time (250mS units) | Acceleration scaling factor | Enable movement stopped events | Enable movement started events
0E1 | ABM | 0E02020000000000 | 2 | 0.5 | +/-2g | Yes | Yes
EF0 | ADR Advanced | Starts with "EF" | ADR ACK limit Unconfirmed mode | ADR ACK delay Unconfirmed mode | ADR ACK limit Confirmed mode | ADR ACK delay Confirmed mode
EF0 | ADR Advanced | EF0A050403000000 | 10 | 5 | 4 | 3
FC0 | Advanced | Starts with "FC" | Rate limit | Port number | Link Quality reporting interval | Link Quality reporting value
FC1 | Advanced | FC00008100000000 | 0 | 0 | Minutes | 1
310 | Advanced IAQ Configuration | Starts with "31" | Pressure Sampling Period | CO2 Sampling Period | ATH Sampling Period | ATH Sampling Period interval | ATH Periodic Reporting value | CO2 Sampling Period interval | CO2 Periodic Reporting value | Pressure Sampling Period interval | Pressure Periodic Reporting value
311 | Advanced IAQ Configuration | 31028105aa | Unchanged | Update | Unchanged | Minutes | 1 | Hours | 5 | Minutes | 42
320 | Advanced IAQ Radio Configuration | Starts with "32" | Port number | Link Quality Period interval | Link Quality Period value | Link Quality attempts | Unconfirmed ADR ACK limit | Unconfirmed ADR ACK delay | Confirmed ADR ACK limit | Confirmed ADR ACK delay
321 | Advanced IAQ Radio Configuration | 320a81ff010a0581 | 10 | Minutes | 1 | 255 | 1 | 10 | 5 | 129
340 | Air Temp & Humidity Sensor Report on Change Configuration | Starts with "34" | Enable RoC reporting | Temperature decrease | Temperature increase | Humidity decrease | Humidity increase
341 | Air Temp & Humidity Sensor Report on Change Configuration | 600516520080030000F2302C39C3A67A563B | Enabled | 22 | 82 | 0 | 128
330 | Air Temp & Humidity Sensor Threshold Configuration | Starts with "33" | Enable threshold reporting | Temperature restoral margin | Low temperature threshold | High temperature threshold | Humidity restoral margin | Low Humidity threshold | High Humidity threshold
331 | Air Temp & Humidity Sensor Threshold Configuration | 600516520080030000F2302C39C3A67A563B | Enabled | 22 | 82 | 0 | 128 | 3 | 0
0D0 | Air Temp Humidity | Starts with "0D" | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease | Temp restoral margin | Humidity restoral margin | Lower Humidity Threshold / Humidity increase | Upper Humidity Threshold / Humidity decrease
0D1 | Air Temp Humidity | 0D00861119301930 | Threshold | Yes | Minutes | 6 | 25 | 48 | 1 | 1 | 25 | 48
360 | CO2 Sensor Report on Change Configuration | Starts with "36" | Enable RoC reporting | CO2 decrease | CO2 increase
361 | CO2 Sensor Report on Change Configuration | 360102030405 | Enabled | 2 | 3
350 | CO2 Sensor Threshold Configuration | Starts with "35" | Enable threshold reporting | Expected CO2 value | CO2 lower limit | CO2 upper limit
351 | CO2 Sensor Threshold Configuration | 3501000300050006 | Enabled | 3 | 5 | 6
ED0 | Device Info Request (Firmware 3.0 or newer) | Only "ED"
ED1 | Device Info Request (Firmware 3.0 or newer) | ED
EB0 | Discard packets | Starts with "EB" | Discard backlog
EB1 | Discard packets | EB01 | Enabled
030 | Door Window | Starts with "03" | Enable Events | Open hold time Seconds (in 250mS steps) | Closed hold time Seconds (in 250mS steps)
031 | Door Window | 0300000100010000 | Yes | 0.25 | 0.25
700 | Dry Contact | Starts with "70" | Enable Contact closed events | Enable Contact open events | Shorted hold time (in 250mS stepps) | Open hold time (in 250mS stepps)
701 | Dry Contact | 0700000200050000 | Yes | Yes | 0.5 | 1.25
010 | General | Starts with "01" | Enable All Events | Enable Adaptive Data Rate | Use Confirmed Messages | Number of Retries | Supervisory reporting interval | Supervisory Period value | Sampling Time interval | Sampling Time value
011 | General | 010007823c000000 | Yes | No | No | 1 | Hours | 130 | 250mS | 15000mS
300 | General IAQ configuration | Starts with "30" | Enable Events | Uplink retries if ACK not received (confirmed mode) | Uplinks: Confirmed or unconfirmed | ADR | Supervisory Period interval | Supervisory Periodic Reporting value | Periodic reporting interval | Periodic Reporting value
301 | General IAQ configuration | 3000030881 | Yes | 0 | Unconfirmed | Disabled | Hours | 8 | Minutes | 1
EE0 | Link Quality | Starts with "EE" | Number of failed confirmed message transmits before a rejoin. 1-255, 0 disables
EE1 | Link Quality | ee06000000000000 | 6
420 | NoX Sensor Report on Change Configuration | Starts with "42" | RoC reporting | NoX Decrease | NoX Increase
421 | NoX Sensor Report on Change Configuration | 420100020003 | Enabled | 2 | 3
410 | NoX Sensor Threshold Configuration | Starts with "41" | Threshold reporting | Expected NoX value | NoX lower limit | NoX upper limit
411 | NoX Sensor Threshold Configuration | 4101000800070006 | Enabled | 8 | 7 | 6
380 | PM 1.0 Sensor Report on Change Configuration | Starts with "38" | RoC reporting | PM 1.0 Decrease | PM 1.0 Increase
381 | PM 1.0 Sensor Report on Change Configuration | 380100010002 | Enabled | 1 | 2
370 | PM 1.0 Sensor Threshold Configuration | Starts with "37" | Threshold reporting | Expected PM 1.0 value | PM 1.0 lower limit | PM 1.0 upper limit
371 | PM 1.0 Sensor Threshold Configuration | 3701000100020003 | Enabled | 1 | 2 | 3
3E0 | PM 10.0 Sensor Report on Change Configuration | Starts with "3E" | RoC reporting | PM 10.0 Decrease | PM 10.0 Increase
3E1 | PM 10.0 Sensor Report on Change Configuration | 3E01000C000D | Enabled | 12 | 13
3D0 | PM 10.0 Sensor Threshold Configuration | Starts with "3D" | Threshold reporting | Expected PM 10.0 value | PM 10.0 lower limit | PM 10.0 upper limit
3D1 | PM 10.0 Sensor Threshold Configuration | 3D010009000a000b | Enabled | 9 | 10 | 11
3A0 | PM 2.5 Sensor Report on Change Configuration | Starts with "3A" | RoC reporting | PM 2.5 Decrease | PM 2.5 Increase
3A1 | PM 2.5 Sensor Report on Change Configuration | 3A0100080009 | Enabled | 8 | 9
390 | PM 2.5 Sensor Threshold Configuration | Starts with "39" | Threshold reporting | Expected PM 2.5 value | PM 2.5 lower limit | PM 2.5 upper limit
391 | PM 2.5 Sensor Threshold Configuration | 3901000500060007 | Enabled | 5 | 6 | 7
3C0 | PM 4.0 Sensor Report on Change Configuration | Starts with "3C" | RoC reporting | PM 4.0 Decrease | PM 4.0 Increase
3C1 | PM 4.0 Sensor Report on Change Configuration | 3C01000C000D | Enabled | 12 | 13
3B0 | PM 4.0 Sensor Threshold Configuration | Starts with "3B" | Threshold reporting | Expected PM 4.0 value | PM 4.0 lower limit | PM 4.0 upper limit
3B1 | PM 4.0 Sensor Threshold Configuration | 3B010009000a000b | Enabled | 9 | 10 | 11
040 | Pulse Counter | Starts with "04" | Periodic Reporting interval | Periodic Reporting value | Threshold sample size | Restoral margin | Overspeed threshold | Underspeed threshold | Too-Long interval | Too-Long value | Debounce Delay
041 | Pulse Counter | 04ffffffffffffffffffff | Minutes | 127 | 75 | 15 | 4095 | 4095 | Minutes | 127 | 1275
060 | Push button | Starts with "06" | Enable hold | Enable released | Enable pressed | Hold delay (in 250mS stepps) | LED Blink on confirmed | LED blink on send | LED when pressed
061 | Push button | 0603080100000000 | Yes | No | No | 2 | Yes | Yes | No
EA0 | Rejoin | Starts with "EA" | Enable discard packets | Enable inportant messages | Enable retain subband | Subband Retries | Message discards
EA1 | Rejoin | EA020A0000000000 | Yes | No | Yes | 10 | 0
EC0 | Restore All Factory Defaults (Firmware 3.0 or newer) | Only "EC"
EC1 | Restore All Factory Defaults (Firmware 3.0 or newer) | EC
200 | Shake-to-send Configuration (Firmware 3.0 or newer) | Starts with "20" | Shake to send events | Scaling factor | Motion Threshold | Settling time (250mS units)
201 | Shake-to-send Configuration (Firmware 3.0 or newer) | 2000010203 | Disabled | +/-4g | 2 | 3
090 | Temp External | Starts with "09" | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Temp restoral margin | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease
091 | Temp External | 09018A020A0A0000 | Report on Change | Yes | Minutes | 10 | 2 | 10 | 10
190 | Temp Internal | Starts with "19" | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Temp restoral margin | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease
191 | Temp Internal | 19008F050A280000 | Threshold | Yes | Minutes | 15 | 5 | 10 | 40
130 | Thermocouple | Starts with "13" | Thermocouple type | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Restoral Margin | Lower Temperature Threshold / Temp increase | Upper Temperature Threshold / Temp decrease
131 | Thermocouple | 13068F05028000A0 | B | Report on Change | Yes | Minutes | 15 | 5 | 40 | 10
0A0 | Tilt | Starts with "0A" | Enable report on change (ROC) to Vertical | Enable ROC to Horizontal | Enable transitions to Vertical | Enable transitions to Horizontal | Angle for transition to Horizontal | Angle for transition to vertical | Vertical hold time (250mS units) | Horizontal hold time (250mS units) | ROC towards Vertical (5-90, 0-4 disables) | ROC towards Horizontal (5-90, 0-4 disables)
0A1 | Tilt | 0A08372301020708 | No | Yes | Yes | Yes | 55 | 35 | 0.25 | 0.5 | 7 | 8
400 | VOC Sensor Report on Change Configuration | Starts with "40" | RoC reporting | VOC Decrease | VOC Increase
401 | VOC Sensor Report on Change Configuration | 400100050007 | Enabled | 5 | 7
3F0 | VOC Sensor Threshold Configuration | Starts with "3F" | Threshold reporting | Expected VOC value | VOC lower limit | VOC upper limit
3F1 | VOC Sensor Threshold Configuration | 3F01000100020003 | Enabled | 1 | 2 | 3
140 | Voltmeter | Starts with "14" | Report on Change/Threshold | Periodic Reporting | Periodic Reporting interval | Periodic Reporting value | Restoral margin 10mV - 2.55V 0 disables | Lower Voltage Threshold / V increase | Upper Voltage Threshold / V decrease
141 | Voltmeter | 1400940A03E804B0 | Threshold | Yes | Minutes | 20 | 0.1 | 10 | 12
080 | Water | Starts with "08" | Enable Events | Threshold | Restoral Margin
081 | Water | 0800690100000000 | Yes | 105 | 1
Note on B1: Filter to your device message type here. Do not sort!

## Downlink Decoder (hidden)
| Packet | Message type | Info1 | Info2 | Info3 | Info4 | Info5 | Info6 | Info7
Downink -> | 13308C05FF000FA00000 | 13 | 30 | 8C | 05 | FF00 | 0FA0
Decoded |  | Thermocouple Temperature Sensor Configuration | Reporting mode Bits 7-5 unused bits 4-1(0000 B Type, 0001 E Type, 0010 J Type, 0011 K Type, 0100 N Type, 0101 R Type, 0110 S Type, 0111 T Type, 1000 Voltage mode Gain=8, Code=8x1.6x217xVIN, 1100 Voltage mode Gain=32, Code=32x1.6x217xVIN) bit 0 (0 Threshold, 1 Report on change) | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | Restoral margin (Threshold mode only) 1-255 with 0 disables. | Upper temperature threshold. Default 90 degrees C (Threshold Mode). Temperature increase (Report on Change Mode) | Lower temperature threshold. Default 90 degrees C (Threshold Mode). Temperature decrease (Report on Change Mode) | 0 | 0
|  |  | Hex2Dec 48 | Hex2Dec 140 | Hex2Dec 5 | Hex2Dec 65280 | Hex2Dec 4000 | Hex2Dec 0 | Hex2Dec 0
|  |  | 00110000 | 10001100 | 00000101 | 1111111100000000 | 0000111110100000 | 0 | 0
|  |  | [1-127] 48 Hrs | [1-127] 12 Min | [1-127] 5 Hrs | #NUM! | #NUM! | [1-127] 0 Hrs | [1-127] 0 Hrs
|  |  | [2s Comp] 48 | [2s Comp] -116 | [2s Comp] 5 | #NUM! | #NUM! | [2s Comp] 0 | [2s Comp] 0
|  |  | [250mS units] 12000 | [250mS units] 35000 | [250mS units] 1250 | [250mS units] 16320000 | [250mS units] 1000000 | [250mS units] 0 | [250mS units] 0
[6 empty] | #NUM! | Thermocouple 250
Thermocouple -16
Examples
Value | Type | Console text | Verified
fc00019800000000 | ADR Advanced | Rate limit: 0x00 Port Number: 0x01 Connectivity Ping Period: 24 Minutes Minutes = 0b1 24 = 0b0011000 | Yes
0100211801000000 | General | Disable all events: No Supervisory Period: 24 Hours Sampling Period: 250 ms Enable Adaptive Data Rate: ADR Disabled Use Confirmed Messages: Yes Uplink retries: 8
01000c1345000000 | General | Disable all events: No 0x00 Radio Config: 0x0C Bit 7 = 0 Bit 6: Duty cycle (EU) = 0 Bits 5-2: Uplink retries = 3 =0b0011 Bit 1: Use Unconfirmed Messages: No = 0 Bit 0: Disable Adaptive Data Rate: ADR Enabled = 0 Supervisory Period: 19 Hours: 0x13 Bits 7-6 : Hours =0b00 Bits 5-0 : 19 = 0b010011 Sampling Period: 5 seconds: 0x45 Bits 7-6 : Seconds =0b01 Bits 5-0: 5 = 0b000101 | Yes
0800690000000000 | Water | Enable water present message: Yes Enable water not present message: Yes Threshold of relative resistance between probes: 105 Restoral margin in units of relative resistance between probes: 0 | Yes
19008f050a280000 | Temp | Config Type : Threshold 0x00 Periodic Reporting: 15 Minutes Minutes = 0b1 15 = 0b000 1111 Restoral margin - Temperature: 5°C 0x05, 0b0000 0101 Lower temperature threshold: 10°C 0b0000 1010 Upper temperature threshold: 40°C 0b0010 1000 | Yes
2001031E14000000 | Shake to send settings | Shake to Send Enable: Yes 01 Accel Scaling Factor: 16g 03 Motion Threshold: 30 1E Settling Time: 5 seconds 5/.25=20 -> 14 | Yes
0100061804000000 | General | Disable all events: No 0x00 Radio Config: 0x06 Bit 7 = 0 Bit 6: Duty cycle (EU) = 0 Bits 5-2: Uplink retries = 1 =0b0001 Bit 1: Use Unconfirmed Messages: Yes = 1 Bit 0: Disable Adaptive Data Rate: ADR Enabled = 0 Supervisory Period: 24 Hours: 0x18 Bits 7-6 : Hours =0b00 Bits 5-0 : 24 = 0b011000 Sampling Period: 1 seconds: 0x04 Bits 7-6 : 250mS =0b00 Bits 5-0: 5 = 0b000100
0100061200000000 | General
FC00011800000000 | ADR Advanced | Rate limit: 0x00 Port Number: 0x01 Connectivity Ping Period: 24 Hours Hours = 0b0 24 = 0b0011000
EE0C000000000000 | Link Quality | 0C 12 attempts before rejoin
EF40200201000000 | ADR Advanced | ADR ACK limit (unconfirmed): 0x40 = 64 ADR ACK Delay (unconfirmed): 0x20 = 32 ADR ACK limit (confirmed): 0x02 = 2 ADR ACK Delay (confirmed): 0x01 = 1
EA02030500000000 | Rejoin Downlink | Flags: 0x02 Enable discard packets: False Enable important messages: True Enable retain subband: False Subband retries: 0x03 = 3 Message Discards: 0x05 = 5
0E05140000000000 | ABM Config | Acceleration change threshold: 0x05 = 5 Settling time: 0x14 250ms increments 20*0.25 = 5 seconds Acceleration scaling factor: 0x00 = +/-2g Disable events bit: 00 (all enabled) Bit 1 disable reporting for movement stopped = 0 Bit 0 disable reporting for movement started = 0
19018F0002020000 | Temp | Config Type : Report on change 0x01 Periodic Reporting: 0x8F = 15 Minutes Minutes = 0b1 15 = 0b000 1111 Restoral margin: 0x00 = disabled Temperature increase: 0x02 = 2 deg C Temperature decrease: 0x02 = 2 deg C
0800502800000000 | Water | Enable water present message: Yes Enable water not present message: Yes Threshold of relative resistance between probes: 0x50 = 80 Restoral margin in units of relative resistance between probes: 0x28 = 40
0D018F0002020505 | ATH | Config Type : Report on change 0x01 Periodic Reporting: 0x8F = 15 Minutes Minutes = 0b1 15 = 0b000 1111 Restoral margin: 0x00 = disabled Temperature increase: 0x02 = 2 deg C Temperature decrease: 0x02 = 2 deg C Humidity increase: 0x05 = 5% Humidity decrease: 0x05 = 5%
0700000000000000 | CON | Disable event flags: 0x00 (all enabled) Disable contact open events: False Disable contact closed events: False Shorted hold time: 0x0000 = 0 Sec Open hold time: 0x0000 = 0 Sec
0600020000000000 | 304
EB01000000000000 | Discard packets
1400000A03E804B0 | Voltmeter | 1400000A03E804B0 14 Voltmeter 00 Threshold 00 Periodic disabled 0A Restoral margin 0.1V 03E8 Lower threshold 10V 04B0 Upper threshold 12V

## Downlink Message types (hidden)
Do not resort, leave sorted by Desc ascending
Type | Bytes | Description | Bits1 | Info1 | Bits2 | Info2 | Bits3 | Info3 | Bits4 | Info4 | Bits5 | Info5 | Bits6 | Info6 | Bits7 | Info7 | Data1 | Data2 | Data3 | Data4 | Data5 | Data6 | Data7
11 | 7 | 4-20mA Current Loop Sensor Configuration | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Restoral margin (Threshold mode only) 10mA-2.55A with 0 disables. | 16 | Lower analog measurement threshold, upper byte (Threshold Mode) Analog measurement increase (Report on Change Mode) | 16 | Upper analog measurement threshold, upper byte (Threshold Mode) Analog measurement decrease (Report on Change Mode)
0E | 4 | Accelerometer-based Motion Sensor Configuration | 8 | Acceleration change threshold (0-127) | 8 | Settling time (in 250mS units) 0-255 | 8 | Acceleration scaling factor (00 2g, 01 4g, 02 8g, 03 16g) | 8 | Disable events Bit(7-2 Unused, 1 disable reporting for movement stopped, 0 disable reporting for movement started)
EF | 4 | ADR Advanced Configuration (Firmware 3.0 or newer) | 8 | ADR ACK limit when in unconfirmed mode | 8 | ADR ACK delay when in unconfirmed mode | 8 | ADR ACK limit when in confirmed mode | 8 | ADR ACK delay when in confirmed mode
FC | 3 | Advanced Configuration | 8 | Rate limit 1-255, 0 disables | 8 | Port number | 8 | Link quality check period, bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables.
31 | 4 | Advanced IAQ Configuration | 8 | Sampling period bit2, 0: Leave Pressure Sampling Period Unchanged 1: Update Pressure Sampling Period bit1,0: Leave CO2 Sampling Period Unchanged 1: Update CO2 Sampling Period bit0,0: Leave ATH Sampling Period Unchanged 1: Update ATH Sampling Period | 8 | ATH sampling period Bit7, 0: Interval Unit in Hours /1: Minutes Bits6-0, 0: Disable Periodic Sampling 1-127: Interval | 8 | CO2 sampling period Bit7, 0: Interval Unit in Hours /1: Minutes Bits6-0, 0: Disable Periodic Sampling 1-127: Interval | 8 | Pressure sampling period Bit7, 0: Interval Unit in Hours /1: Minutes Bits6-0, 0: Disable Periodic Sampling 1-127: Interval
32 | 7 | Advanced IAQ Radio Configuration | 8 | Bits7-0, 1-127: Port Number | 8 | Link Quality Period Bit7, 0: Period Interval in Hours / 1: Minutes Bits6-0, 0: Disable Link Quality Message 1-127: Interval | 8 | Link Quality attempts 0-255 | 8 | Unconfirmed ADR ACK Limit 1-127 | 8 | Unconfirmed ADR ACK Delay 1-127 | 8 | Confirmed ADR ACK Limit 1-127 | 8 | Confirmed ADR ACK Delay 1-127
34 | 4 | Air Temp & Humidity Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 8 | Temperature Decrease 0-255 (C) | 8 | Temperature Increase 0-255 (C) | 8 | Humidity Decrease 0-255 (%) | 8 | Humidity Increase 0-255 (%)
33 | 5 | Air Temp & Humidity Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 8 | Temperature restoral margin 0-255 (C) | 8 | Absolute Temp for Lower Threshold 0-255 (C) | 8 | Absolute Temp for Upper Threshold 0-255 (C) | 8 | Humidity restoral margin 0-255 (C) | 8 | Absolute Humidity for Lower Threshold 0-255 (%) | 8 | Absolute Humidity for Upper Threshold 0-255 (%)
0D | 7 | Air Temp and Humidity Sensor Configuration | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Restoral margin (Threshold mode only) 1-15 with 0 disables. | 8 | Absolute Temperature for Lower Threshold (Threshold Mode) or Relative Temperature Increase (Report on Change Mode) | 8 | Absolute Temperature for Upper Threshold (Threshold Mode) or Relative Temperature Decrease (Report on Change Mode) | 8 | Absolute Humidity for Lower Threshold (Threshold Mode) or Relative Humidity Increase (Report on Change Mode) | 8 | Absolute Humidity for Upper Threshold (Threshold Mode) or Relative Humidity Decrease (Report on Change Mode)
36 | 4 | CO2 Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | CO2 Decrease 0-65535 PPM | 16 | CO2 Increase 0-65535 PPM
35 | 6 | CO2 Sensor Threshold Configuration | 8 | CO2 Threshold config Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected CO2 value 0-65535 PPM | 16 | CO2 Lower limit 0-65535 PPM | 16 | CO2 Upper limit 0-65535 PPM
ED | 1 | Device Info Request (Firmware 3.0 or newer) | 8 | Report current sensor configurations
EB | 1 | Discard packets | 8 | 01 = discard backlog
03 | 5 | Door/Window Sensor Configuration | 8 | All events (00 enable, 01 disable) | 16 | Open hold time (in 250mS units) 0-65535 | 16 | Closed hold time (in 250mS units) 0-65535
07 | 5 | Dry Contact Sensor Configuration | 8 | Disable events Bit(7-2 Unused, 1 disable contact open events, 0 disable contact closed events) | 16 | Shorted hold time (in 250mS units) 0-65535 | 16 | Open hold time (in 250mS units) 0-65535
01 | 4 | General Configuration | 8 | All events (00 enable, 01 disable) | 8 | Radio Config Bit(7 not used, 6 Enable duty cycle req, 5-2 Uplink retries (range 0-8), 1 Use unconfirmed messages =1, 0 Disable ADR =1) | 8 | Super period bits(7 {Hours=0 ,Min=1}, 6-0 Value from 1-127) | 8 | Sampling rate (Bits 7-6 Increments of {00 250mS, 01 Sec, 10 Min, 11 Hrs}, 5-0 Value from 1-63)
30 | 4 | General IAQ Configuration | 8 | All events (00 enable, 01 disable) | 8 | bits5-2, 1-8: Number of Uplink Retries if ACK not received, only for confirmed uplinks bit1, 0: Confirmed / 1: Unconfirmed Uplinks bit0, 0: Enable / 1: Disable Adaptive Data Rate | 8 | bit7, 0: Supervisory period interval in Hours /1: Minutes bits6-0, 0: Disable Supervisory Message 1-127: Interval | 8 | Bit 7, 0: Periodic reporting Interval Unit Hours / 1: Minutes bits 6-0,0: Disable Periodic Reporting 1-127: Interval
1C-1F | 7 | High-bandwidth Vibration Sensor Configuration (channel 1-4)
0F | 7 | High-precision Tilt Sensor Configuration | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Hold time, units of 250mS. 0-255. 0 disables | 8 | Angle for transition from 0 degree vertical integer value (0-180) | 8 | Angle for transition from 0 degree vertical fractional value (0-??) | 8 | Angle for transition toward 0 degree vertical integer value (0-180) | 8 | Angle for transition toward 0 degree vertical fractional value (0-??)
EE | 1 | Link Quality Configuration (Firmware 3.0 or newer) | 8 | Number of failed confirmed message transmits before the device does a rejoin. 1-255, 0 disables
42 | 4 | NoX Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | NoX Decrease 0-65535 PPM | 16 | NoX Increase 0-65535 PPM
41 | 6 | NoX Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected NoX value 0-65535 PPM | 16 | NoX Lower limit 0-65535 PPM | 16 | NoX Upper limit 0-65535 PPM
38 | 4 | PM 1.0 Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | PM 1.0 Decrease 0-65535 PPM | 16 | PM 1.0 Increase 0-65535 PPM
37 | 6 | PM 1.0 Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected PM 1.0 value 0-65535 PPM | 16 | PM 1.0 Lower limit 0-65535 PPM | 16 | PM 1.0 Upper limit 0-65535 PPM
3E | 4 | PM 10.0 Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | PM 10.0 Decrease 0-65535 PPM | 16 | PM 10.0 Increase 0-65535 PPM
3D | 6 | PM 10.0 Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected PM 10.0 value 0-65535 PPM | 16 | PM 10.0 Lower limit 0-65535 PPM | 16 | PM 10.0 Upper limit 0-65535 PPM
3A | 4 | PM 2.5 Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | PM 2.5 Decrease 0-65535 PPM | 16 | PM 2.5 Increase 0-65535 PPM
39 | 6 | PM 2.5 Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected PM 2.5 value 0-65535 PPM | 16 | PM 2.5 Lower limit 0-65535 PPM | 16 | PM 2.5 Upper limit 0-65535 PPM
3C | 4 | PM 4.0 Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | PM 4.0 Decrease 0-65535 PPM | 16 | PM 4.0 Increase 0-65535 PPM
3B | 6 | PM 4.0 Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected PM 4.0 value 0-65535 PPM | 16 | PM 4.0 Lower limit 0-65535 PPM | 16 | PM 4.0 Upper limit 0-65535 PPM
04 |  | Pulse Counter | 8 | Reporting period Bit7, 0: Interval Unit in Hours /1: Minutes Bits6-0, 0: Disable Periodic Sampling 1-127: Interval | 8 | Threshold sample size (multiples of 10) | 8 | Restoral margin (pps) | 8 | Overspeed threshold (pps) | 8 | Underspeed threshold (pps) | 8 | Too-long time Bit7, 0= Seconds 1=Minutes Bits 6-0, Length
06 | 3 | Push Button Sensor Configuration | 8 | Disable events Bit(7-3 Unused, 2 Disable hold, 1 disable released, 0 disable pressed) | 8 | Hold delay (in 250mS units) 0-20 | 8 | LED config bits(7-3 unused, 2 disable blink on confirmed, 1 Disable blink on send, 0 Disable LED on when pressed)
EA | 8 | Rejoin Downlink | 8 | Bits 7-3 Reserved 2 Enable discard packets flag 1 Enable important messages flag 0 Enable retain subband flag | 8 | Subband retries | 8 | Message discards | 24 | Reserved
EC | 0 | Restore All Factory Defaults (Firmware 3.0 or newer)
20 | 4 | Shake-to-send Configuration (Firmware 3.0 or newer) | 8 | Shake to send events (00 disable, 01 enable) | 8 | Scaling factor (00 2g, 01 4g, 02 8g, 03 16g) | 8 | Motion threshold (0-127) | 8 | Settling time units of 250mS (0-255)
09 | 7 | Temp External | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Restoral margin (Threshold mode only) 1-15 C with 0 disables. | 8 | Absolute Temperature for Lower Threshold (Threshold Mode) or Relative Temperature Increase (Report on Change Mode) | 8 | Absolute Temperature for Upper Threshold (Threshold Mode) or Relative Temperature Decrease (Report on Change Mode)
19 | 7 | Temp Internal | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Restoral margin (Threshold mode only) 1-15 C with 0 disables. | 8 | Absolute Temperature for Lower Threshold (Threshold Mode) or Relative Temperature Increase (Report on Change Mode) | 8 | Absolute Temperature for Upper Threshold (Threshold Mode) or Relative Temperature Decrease (Report on Change Mode)
13 | 7 | Thermocouple Temperature Sensor Configuration | 8 | Reporting mode Bits 7-5 unused bits 4-1(0000 B Type, 0001 E Type, 0010 J Type, 0011 K Type, 0100 N Type, 0101 R Type, 0110 S Type, 0111 T Type, 1000 Voltage mode Gain=8, Code=8x1.6x217xVIN, 1100 Voltage mode Gain=32, Code=32x1.6x217xVIN) bit 0 (0 Threshold, 1 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Restoral margin (Threshold mode only) 1-255 with 0 disables. | 16 | Upper temperature threshold. Default 90 degrees C (Threshold Mode). Temperature increase (Report on Change Mode) | 16 | Lower temperature threshold. Default 90 degrees C (Threshold Mode). Temperature decrease (Report on Change Mode)
0A | 7 | Tilt Sensor Configuration | 8 | Disable events Bit(7-4 Unused, 3 Disable report on change toward vert, 2 Disable report on change toward horiz, 1 disable transitions to vert, 0 disable transitions to horiz) | 8 | Angle for transition to Horiz (0-90) | 8 | Angle for transition to Vert (0-90) | 8 | Vertical hold time, units of 250mS. 0-255. 0 disables | 8 | Horizontal hold time, units of 250mS. 0-255. 0 disables | 8 | Report on change towards vertical (5-90) 0-4 disables | 8 | Report on change towards horizontal (5-90) 0-4 disables
10 | 7 | Ultrasonic Distance Sensor Configuration | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Hold time bits(7 {Min 0, Sec 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Lower distance threshold in mm, upper byte. Default 100mm (Threshold Mode) Distance increase in mm, upper byte (Report on Change Mode) | 8 | Lower distance threshold in mm, lower byte. Default 100mm (Threshold Mode) Distance increase in mm, lower byte (Report on Change Mode) | 8 | Upper distance threshold in mm, upper byte. Default 100mm (Threshold Mode) Distance increase in mm, upper byte (Report on Change Mode) | 8 | Upper distance threshold in mm, lower byte. Default 100mm (Threshold Mode) Distance increase in mm, lower byte (Report on Change Mode)
40 | 4 | VOC Sensor Report on Change Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable RoC Reporting 1: Enable RoC Reporting | 16 | VOC Decrease 0-65535 PPM | 16 | VOC Increase 0-65535 PPM
3F | 6 | VOC Sensor Threshold Configuration | 8 | Bits7-1, Reserved Bit0, 0: Disable Threshold Reporting 1: Enable Threshold Reporting | 16 | Expected VOC value 0-65535 PPM | 16 | VOC Lower limit 0-65535 PPM | 16 | VOC Upper limit 0-65535 PPM
14 | 7 | Voltmeter Sensor Configuration | 8 | Reporting mode (00 Threshold, 01 Report on change) | 8 | Periodic reporting bits(7 {Hrs 0, Min 1}, 6-0 Value from 1-127) Value of 0 disables. | 8 | Restoral margin (Threshold mode only) 10mV-2.55V with 0 disables. | 16 | Lower analog measurement threshold, upper byte (Threshold Mode) Analog measurement increase (Report on Change Mode) | 16 | Upper analog measurement threshold, upper byte (Threshold Mode) Analog measurement decrease (Report on Change Mode)
08 | 3 | Water Sensor Configuration | 8 | Disable events Bit(7-2 Unused, 1 disable water not present events, 0 disable water present events) | 8 | Threshold | 8 | Restoral margin

## MTCT300
Data | Packet ID | Amp-Hour Accumulation | Amps-RMS-Avg | Max Scalar | Min Scalar | Cap voltage scalar | Temp scalar | Bit Breakdown | [6 empty] | dAh | [5 empty] | dA
600516520080030000F2302C39C3A67A563B | 96 | 8534886.4 | 3277.1 | 3277.1 | 3277.1 | 4.7451 | -17.4118 |  | PID |  | Amp-Hour accumulation | [7 empty] | Amps RMS |  |  |  | Max |  | Min |  | CapV |  | Temp
[9 empty] | 6 | 0 | 0 | 5 | 1 | 6 | 5 | 2 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | F | 2 | 3 | 0

## SW version differences
Type | Message info | Effective SW version | Change
Uplink | Reset message, FW version | 2.0 | Human-readable in firmware versions prior to 2.0, where 0x0103 would represent version 1.3. From 2.0 onward, the firmware version is formatted as a three digit version number
Downlink | General config, Radio config | 2.2.1 | Bit 6: Enable duty cycle requirement (LoRaWAN EU868 only). Set the enable duty cycle requirement to enforce the EU868 band duty cycle requirements. Default is clear / disabled. It is required to enable this prior to production deployment. Available in firmware 2.2.1 or later.
Downlink | General config, Radio config | 1.4 | Number of uplink retries if ACK not received on confirmed uplink. The range for uplink retries is 1-8 for confirmed messages (ack required) and does not apply to unconfirmed messages. Default 0 (leave unchanged). Available in firmware v1.4 and above.
Downlink | General config, Radio config | 1.4 | Use unconfirmed messages. If the use unconfirmed messages bit is set, the sensor will not look for an ack from the network server. Default is 1 (unconfirmed messages, no acks required). EU sensors cannot use confirmed messages, and thus setting this bit to 0 on an EU device will result in an error. Available in firmware v1.4 and above.
Downlink | General config, Radio config | 1.3 | Disable Adaptive Data Rate. Set the disable adaptive data rate bit to disable ADR, clear to enable ADR. Default is 0 (enabled). Available in firmware v1.3 and above.
Downlink | Advanced config, Port number | 1.4 | Port Number. Changes the uplink port per the LoRaWAN protocol. The default port is 2, and a value of 0 in this field means to leave it at the default. This feature is available in firmware v1.4 and above.
Downlink | Advanced config, Link quality check | 2.0 | Link Quality Check Period. Setting this register causes the device to “ping” the network server on a periodic basis with a requested ack to ensure the device is still connected. This is implemented as a confirmed message containing connectivity info, and is typically used in conjunction with unconfirmed messages. In other words, while running with unconfirmed messages, this feature will create a periodic confirmed message and look for the ack to ensure connectivity. A value of 0x00 means disable the connectivity period feature. Available in firmware v2.0 and above. The Link Quality period in byte 2 is defined in the following table.